Flatness-Based and Passivity-Based Control with Adaptive RBF Neural Compensation of a 2 MW Direct-Drive PMSG Wind Energy Conversion System

Said Regani, Manal Messadi and Karim Kemih*

L2EI Laboratory, Jijel University, BP 98, Ouled Aissa, Jijel 18000, Algeria;

said.regani@univ-jijel.dz (S.R.); manal.messadi@univ-jijel.dz (M.M.)

* Correspondence: karim_kemih@univ-jijel.dz

Abstract: This paper proposes a nonlinear control scheme with adaptive radial basis function (RBF) neural compensation for a 2 MW direct-drive wind energy conversion system based on a permanent magnet synchronous generator (PMSG) connected to the grid through a back-to-back converter and an L filter. First, a complete model of the system, from the wind to the grid, is established in the receptor convention, and its signs are verified by an exact power balance. Subsequently, the rotor speed and the energy stored in the DC link and in the filter are used as flat outputs of the two outer loops, and the currents of both converters are controlled by passivity-based control (PBC), whose convergence is proved with a storage function. To further enhance the speed tracking, an RBF network is introduced as a complementary compensation of the aerodynamic-torque and parameter uncertainty, without retuning the nominal gains. A Lyapunov-based adaptation law with σ-modification guarantees the uniform ultimate boundedness of the speed error and of the network weights. The scheme is evaluated with step and turbulent wind, parameter mismatch, a 50 % grid voltage dip, sensor noise and grid voltage harmonics. Simulation results show that all the controlled variables track their references, that the DC-link voltage remains within 0.8 % of its reference outside the dip, that the grid-current distortion stays below 4 %, and that the neural compensation reduces the integral absolute speed error by 26.5 to 44.8 % with the same captured energy.

Keywords: wind energy conversion systems; direct-drive PMSG; differential flatness; passivity-based control; adaptive RBF neural network; back-to-back converter

# 1. Introduction

The increasing demand for clean energy and the need to reduce greenhouse gas emissions have made wind energy one of the main sources of the transition towards low-carbon electricity generation. Barthelmie and Pryor [1] discussed the contribution of wind energy to climate-change mitigation, and the reports of the International Energy Agency [2] and of the Global Wind Energy Council [3] show the continuous growth of the installed capacity. This growth is accompanied by larger turbines and by stricter requirements on the quality of the injected power.

Among the generator technologies used in variable-speed wind turbines, the direct-drive permanent magnet synchronous generator (PMSG) has become an important solution. Polinder et al. [4] reviewed the trends in wind turbine generator systems and showed that removing the gearbox reduces maintenance and mechanical losses. Yaramasu et al. [5] and Wu et al. [6] described the full-scale back-to-back converter of these turbines: the machine-side converter (MSC) controls the generator torque to track the maximum power point, and the grid-side converter (GSC) regulates the DC-link voltage and injects the power into the grid. Since the whole power flows through the converter, the generator is fully decoupled from the grid. Rolán et al. [7] and Hasan and Shatil [8] presented the modeling and the design of grid-connected PMSG wind turbines, which provide the data used in the present study.

These control tasks are usually performed by cascaded proportional-integral (PI) loops in rotating reference frames. Chinchilla et al. [9] applied this vector control to permanent-magnet generators connected to the grid, and Yazdani and Iravani [10] and Blaabjerg et al. [11] detailed the modeling, the current control and the grid synchronization of voltage-sourced converters. The PI loops are simple and robust, but they are tuned on a linearized model and do not use the nonlinear structure of the system.

Considerable research has therefore been devoted to nonlinear control of wind energy conversion systems. Mechter et al. proposed a sliding mode control with an exponential reaching law [12] and a backstepping control for low wind speeds [13]. For the PMSG, Messadi et al. [14] developed a predictive control of a chaotic PMSG in a wind turbine, Yang et al. [15] designed a fuzzy state-feedback control of a fractional-order direct-drive PMSG with uncertain parameters, and Benabdeeseelam et al. [16] proposed a chattering-free terminal sliding mode control for a chaotic PMSG in an offshore wind turbine. Among the model-based methods, differential flatness [17] computes the control directly from the desired trajectory of a flat output. Aimene et al. [18] compared flatness-based and field-oriented control of a grid-connected PMSG wind energy conversion system, and Thounthong et al. [19] showed that, with the stored energy as flat output, the DC-bus dynamics become a linear power balance. Passivity-based control (PBC) [20, 21] shapes the energy of the closed loop and keeps the workless coupling terms of electrical machines, which makes it well suited to the current loops of the converters.

Learning-based approximators have also been exploited to handle the uncertainty of wind turbine models. RBF networks are universal approximators [22], and their weights can be adapted online with a Lyapunov-based law [23]. Li et al. [24] introduced an RBF neural network-based global fast terminal sliding mode control for a fully controlled doubly-fed induction generator, Dardabi et al. [25] used artificial neural networks to enhance the control of doubly-fed induction generators in the presence of real wind profiles, and Bounar et al. [26] proposed a disturbance-observer-based finite-time adaptive neural control of a doubly-fed induction generator wind turbine. In our previous work [27], a nonlinear state-feedback controller was combined with an adaptive artificial neural network that compensates the residual tracking error of a doubly-fed induction generator; that study did not consider measurement noise or grid disturbances.

These studies show that nonlinear, adaptive and neural methods can improve the performance of wind energy conversion systems. However, the existing works generally address one converter or one loop, and the flatness-based and passivity-based methods use a model whose weak point is the aerodynamic torque, which is not measured, and the generator parameters, which change with temperature and saturation. In particular, increasing the gains of the speed loop is not an appropriate way to reduce the effect of this uncertainty, because the speed loop multiplies the measurement noise by the large inertia of the turbine. A control framework that combines flatness for the outer loops, PBC for the current loops of both converters and an adaptive neural compensation of the aerodynamic uncertainty, and that is evaluated under realistic measurements and grid disturbances, remains less explored.

Motivated by this gap, the present study proposes a flatness-based and passivity-based control with adaptive RBF neural compensation for a 2 MW direct-drive PMSG wind energy conversion system. The neural network does not replace the nominal controller; it adds a compensation term to the flat speed law, and the nominal gains are kept unchanged. The main contributions of this work are summarized as follows:

- Complete and verified model: the system is modeled from the wind to the grid in the receptor convention, and an exact power balance verifies the sign of every term of the model.

- Flatness-based outer loops: the rotor speed and the energy stored in the DC link and in the filter are used as flat outputs, so that the DC-link dynamics become a linear power balance.

- Passivity-based current loops: the currents of both converters are controlled by PBC, and their convergence is proved with a storage function and Barbalat’s lemma.

- Adaptive RBF compensation: an RBF network learns online the aerodynamic-torque and parameter uncertainty with a Lyapunov-based law with σ-modification, and the uniform ultimate boundedness of the speed error and of the weights is established.

- Realistic numerical validation: the control is evaluated with the same nominal gains without and with the network, under step and turbulent wind, parameter mismatch, sensor noise, grid voltage harmonics and a 50 % voltage dip.

The remainder of this paper is organized as follows. Section 2 presents the mathematical modeling of the PMSG wind energy conversion system. Section 3 describes the proposed flatness-based and passivity-based control and its stability analysis. Section 4 presents the adaptive RBF compensation and the corresponding uniform-ultimate-boundedness analysis. Section 5 presents the numerical simulations and discusses the results. Finally, Section 6 concludes the paper and outlines directions for future work.

# 2. Mathematical Modeling of the PMSG Wind Energy Conversion System

The studied system is shown in Figure 1. The turbine drives the PMSG directly; the MSC rectifies the generator voltages, the DC link decouples the two converters, and the GSC injects the power into the 690 V, 50 Hz grid through an L filter. The parameters of the system are given in Table 1.

Figure 1. Direct-drive PMSG wind energy conversion system with a back-to-back converter.

## 2.1. Wind Turbine Aerodynamic Modeling

The power captured by the rotor and the tip-speed ratio are [28, 18]

|  | Pw=12ρπR2Cpλ,β v3, λ=ΩRv, | (1) |
| --- | --- | --- |

where ρ is the air density, R the rotor radius, v the wind speed, Ω the rotor speed and β the pitch angle. The power coefficient is

|  | Cp=0.5176116λi−0.4β−5e−21/λi+0.0068λ, 1λi=1λ+0.08β−0.035β3+1. | (2) |
| --- | --- | --- |

For β=0, Cp reaches its maximum Cp,max=0.48 at λopt=8.1 (Figure 2). The aerodynamic torque is Tw=Pw/Ω. For Pn=2 MW and R=40 m, close to the 2 MW turbine of [7], the rated wind speed given by Pn=12ρπR2Cp,maxvn3 is vn=11.0 m/s, the rated speed is Ωn=λoptvn/R=2.23 rad/s and the rated torque is Tn=Pn/Ωn=0.897 MN⋅m. Since the wind speed considered in this study remains below vn, the pitch angle is kept at zero.

Figure 2. Power coefficient for β=0 (left) and captured power versus rotor speed with the maximum power curve (right).

## 2.2. Electrical Modeling of the PMSG

In the rotor dq frame (amplitude-invariant transformation, d axis aligned with the magnet flux), with the receptor convention and Ld=Lq=Ls [18], the stator voltages and the electromagnetic torque are

|  | vsd=Rsisd+Lsdisddt−ωeLsisq, | (3) |
| --- | --- | --- |

|  | vsq=Rsisq+Lsdisqdt+ωeLsisd+ωeψf, | (4) |
| --- | --- | --- |

|  | Te=32p ψf isq, | (5) |
| --- | --- | --- |

where ωe=pΩ is the electrical speed, p the number of pole pairs and ψf the magnet flux. In the receptor convention, Te<0 and isq<0 in generating mode. With is=isd isqT, vs=vsd vsqT, eq=0 1T and the skew-symmetric matrix J=01−10, (3)–(4) are written in the compact form

|  | Lsis=vs−Rsis+ωeLsJis−ωeψfeq. | (6) |
| --- | --- | --- |

The generator data are those of the non-salient 2 MW PMSG of [8]. At Ωn, the back-electromotive force pΩnψf=532 V is close to the peak phase voltage of the grid (563 V).

## 2.3. Mechanical Dynamics

The direct-drive shaft is described by the one-mass model

|  | JdΩdt=Tw+Te−BΩ, | (7) |
| --- | --- | --- |

where J is the total inertia of the turbine and generator and B the friction coefficient.

## 2.4. Back-to-Back Converter and DC Link

The two-level converters are represented by their average model, with voltage vectors limited to the linear range Vdc/3 of the space-vector modulation. The DC link receives the power of the MSC and supplies the GSC [18]:

|  | CVdcdVdcdt=Pdc−Pi, Pdc=−32vsTis, Pi=32viTig, | (8) |
| --- | --- | --- |

where vi is the GSC voltage and ig the grid current.

## 2.5. L Filter and Grid

In the grid-voltage-oriented frame (vgq=0), with the current counted from the converter towards the grid [18],

|  | Lfig=vi−Rfig+ωgLfJig−vg, | (9) |
| --- | --- | --- |

where ωg is the grid angular frequency, and the grid powers are Pg=32vgdigd and Qg=−32vgdigq.

## 2.6. Power Balance of the Model

With the total stored energy E=12JΩ2+34Ls∥is∥2+12CVdc2+34Lf∥ig∥2, and since xTJx=0 for any x and TeΩ=32ωeψfisq, the model (1)–(9) gives, for any state and any converter voltages,

|  | E=Pw−BΩ2−32Rs∥is∥2−32Rf∥ig∥2−Pg. | (10) |
| --- | --- | --- |

The captured power is therefore stored, dissipated in the friction and in the resistances, or injected into the grid. This balance verifies the sign of every term of the model; its numerical residual, evaluated at random states and inputs, is below 10−15Pn.

Table 1. Parameters of the studied system.

| Parameter | Symbol | Value | Source |
| --- | --- | --- | --- |
| Rated power | Pn | 2 MW | [8] |
| Rotor radius | R | 40 m | [7] |
| Air density | ρ | 1.225 kg/m3 | [18] |
| Rated wind speed / rotor speed | vn, Ωn | 11.0 m/s, 2.23 rad/s | (1) |
| Total inertia | J | 2.8×106 kg⋅m2 | assumed |
| Friction coefficient | B | 103 N⋅m⋅s | assumed |
| Pole pairs | p | 26 | [8] |
| Stator resistance | Rs | 0.78 mΩ | [8] |
| Stator inductance | Ls | 1.57 mH | [8] |
| Magnet flux | ψf | 9.18 Wb | [8] |
| DC-link capacitance and voltage | C, Vdc* | 20 mF, 1200 V | [8] |
| Filter inductance and resistance | Lf, Rf | 0.15 mH, 2 mΩ | [8], assumed |
| Grid voltage and frequency |  | 690 V, 50 Hz | [8] |
| Switching frequency | fsw | 2160 Hz | [8] |

# 3. Proposed Flatness-Based and Passivity-Based Control

In this article, the outer loops are designed by differential flatness and the current loops by passivity-based control. The objective of this combination is to compute the references directly from the model, so that the generator power is passed to the grid without waiting for an error on the DC-link voltage, while the current loops keep the energy structure of the machine and of the filter. The architecture of the proposed control is presented in Figure 3. All the errors are defined as measured minus reference values. The controller is sampled at Ts=1/2fsw=231.5 μs, and the converter voltages are applied one sample after their computation.

Figure 3. Structure of the proposed control: flat outer loops, PBC current loops and adaptive RBF compensation.

## 3.1. MPPT Reference

The optimal rotor speed Ωopt=λoptvm/R, computed from the anemometer measurement vm and limited to 0.5Ωn,Ωn, is filtered by the second-order model

|  | Ω*=ωr2Ωopt−Ω*−2ωrΩ*, | (11) |
| --- | --- | --- |

with ωr=1 rad/s, which gives a smooth reference Ω* and its derivative Ω*.

## 3.2. Flatness-Based Speed Loop

From (7), Te=JΩ+BΩ−Tw: the rotor speed Ω is a flat output of the shaft with input Te, i.e., isq [17, 18]. Imposing Ω=ν1 with

|  | ν1=Ω*−k11eΩ−k12​∫​eΩ dt, eΩ=Ω−Ω*, | (12) |
| --- | --- | --- |

gives the torque and current references

|  | Te*=Jν1+BΩ−Tw−Δ, isq*=Te*32pψf, isd*=0, | (13) |
| --- | --- | --- |

where Tw is computed from (1)–(2) with vm, and Δ is the neural compensation of Section 4 (Δ=0 for the nominal controller). Te* is limited to −1.2Tn,0, with the integration frozen at the limit. With isq=isq* and Δ=Tw−Tw, the speed error obeys

|  | JeΩ+k11eΩ+k12​∫​eΩ dt=Δ−Δ. | (14) |
| --- | --- | --- |

## 3.3. Flatness-Based DC-Link Loop

The flat output of the DC-link loop is the energy stored in the DC link and in the filter, y2=12CVdc2+34Lf∥ig∥2. From (8)–(9),

|  | y2=Pdc−Pg−32Rf∥ig∥2, | (15) |
| --- | --- | --- |

which is linear in the grid power [19]. Imposing y2=−k21ey−k22∫ey dt, with ey=y2−y2* and y2*=12CVdc*2+34Lf∥ig*∥2, gives

|  | Pg*=Pdc−32Rf∥ig∥2+k21ey+k22​∫​ey dt, igd*=2Pg*3vgd, igq*=0, | (16) |
| --- | --- | --- |

where igq*=0 gives a unity power factor. Pdc is computed from the applied MSC voltages and the measured currents, so that the generator power is passed to the grid before it changes Vdc.

## 3.4. Passivity-Based Current Loops

With es=is−is* and zs=es, the MSC voltage reference is

|  | vs*=Lsis*+Rsis*−ωeLsJis*+ωeψfeq−Raes−Kizs, | (17) |
| --- | --- | --- |

and, with eg=ig−ig* and zg=eg, the GSC voltage reference is

|  | vi*=Lfig*+Rfig*−ωgLfJig*+vg−Rbeg−Kigzg. | (18) |
| --- | --- | --- |

The first terms of (17)–(18) reproduce the desired dynamics with the workless coupling terms, Ra and Rb inject damping, and the integral terms remove the steady-state errors. The reference derivatives are obtained by first-order filters with a time constant of 2 ms, and the integrals are frozen when the voltage reaches Vdc/3.

Theorem 1. Consider the PMSG model (6) with the control (17) and Ra,Ki>0. The storage function H=12Ls∥es∥2+12Ki∥zs∥2 satisfies H=−Rs+Ra∥es∥2≤0, and es→0. The same result holds for the filter (9) with the control (18).

Proof. Subtracting Lsis* from (6) and inserting (17) gives the error dynamics

|  | Lses=−Rs+Raes+ωeLsJes−Kizs. | (19) |
| --- | --- | --- |

Hence H=esTLses+KizsTes=−Rs+Ra∥es∥2, since esTJes=0. H is therefore non-increasing and bounded, es and zs are bounded, and H is uniformly continuous. Barbalat’s lemma [29] gives es→0. The proof for (9) and (18) is identical, with Lf, Rf+Rb and Kig. ▫

The gains place double closed-loop poles: k11=2ωΩ, k12=ωΩ2, k21=2ωv, k22=ωv2, Rs+Ra=2ωiLs, Ki=ωi2Ls, Rf+Rb=2ωiLf and Kig=ωi2Lf. The bandwidths are separated by more than one decade (ωΩ=2, ωv=60 and ωi=500 rad/s), so the inner loops can be considered fast with respect to the outer ones (Table 2).

# 4. Adaptive RBF Neural Compensation

Although the nominal controller makes the current errors converge, a residual speed error remains because of the uncertainty Δ=Tw−Tw in (14). This uncertainty comes from the Cp model, from the anemometer, which measures the wind at one point and with a delay, and from the generator parameters. Therefore, an RBF network is introduced as a complementary compensation mechanism. The network does not replace the nominal controller; it generates the additional term Δ in the torque reference (13), and the gains k11, k21, k22 and those of the current loops are kept unchanged.

## 4.1. ANN Input Vector

The uncertainty Δ depends mainly on the operating point of the turbine, i.e., on the rotor speed and on the wind speed. The input vector of the network is therefore

|  | z=ΩΩn vmvnT, | (20) |
| --- | --- | --- |

where the normalization by the rated values gives inputs of the order of one over the whole operating region.

## 4.2. RBF Structure and Compensation Signal

On the operating region, the uncertainty is approximated by

|  | Δ=W*Tϕz+ε, ε≤ε, | (21) |
| --- | --- | --- |

where W* is an ideal weight vector and ε the approximation error [22]. The network has 25 Gaussian functions

|  | ϕjz=exp−∥z−cj∥22b2, j=1,…,25, | (22) |
| --- | --- | --- |

centred on a 5×5 grid of 0.5,1.12, with the width b=0.15. The compensation signal is

|  | Δ=WTϕz, | (23) |
| --- | --- | --- |

where W is the vector of the estimated weights. When the network is used, it replaces the integral action of the speed loop (k12=0): otherwise, the integral would absorb the slowly varying part of Δ and the network would not learn it.

## 4.3. Online Adaptive Law

The weights are not trained offline; they are adapted online by the Lyapunov-based law

|  | W=Γϕz eΩ−σW, W0=0, | (24) |
| --- | --- | --- |

where Γ>0 is the adaptation gain and σ>0 the σ-modification [30], which limits the drift of the weights in the presence of noise and approximation error. The adaptation is frozen when Te* reaches its limit, so that the network does not learn the effect of the saturation.

## 4.4. Bounded Adaptive Compensation

Theorem 2. Consider the speed error dynamics (14) with k12=0, the approximation (21), the compensation (23) and the adaptive law (24) with Γ,σ>0, exact J and B, and no saturation. Then the speed error eΩ and the weight error W=W*−W are uniformly ultimately bounded.

Proof. With k12=0, (14) becomes JeΩ=−Jk11eΩ+WTϕ+ε. Consider the Lyapunov function

|  | V=12JeΩ2+12Γ∥W∥2. | (25) |
| --- | --- | --- |

Since W=−W,

|  | V=−Jk11eΩ2+eΩWTϕ+ε−1ΓWTW=−Jk11eΩ2+eΩε+σWTW. | (26) |
| --- | --- | --- |

Using WTW≤12∥W*∥2−12∥W∥2 and eΩε≤Jk112eΩ2+ε22Jk11 gives

|  | V≤−Jk112eΩ2−σ2∥W∥2+ε22Jk11+σ2∥W*∥2, | (27) |
| --- | --- | --- |

which is negative outside a compact set. Hence eΩ and W are uniformly ultimately bounded [29]. ▫

Remark 1. The size of the residual set decreases when k11 increases and when σ and ε decrease. Increasing k11 would, however, amplify the measurement noise by Jk11 in (13); the network reduces the speed error without changing this gain.

Table 2. Controller, adaptive network and measurement parameters used in the simulations.

| Parameter | Value |
| --- | --- |
| Speed loop (flat) | ωΩ=2 rad/s: k11=4, k12=4 (0 with the network); ωr=1 rad/s |
| DC-link loop (flat) | ωv=60 rad/s: k21=120, k22=3600 |
| PBC, MSC | ωi=500 rad/s: Ra=1.57 Ω, Ki=393 Ω/s |
| PBC, GSC | ωi=500 rad/s: Rb=0.148 Ω, Kig=37.5 Ω/s |
| RBF network | 25 Gaussian units, b=0.15, inputs (20) |
| Adaptation | Γ=107, σ=0.02 s-1, W0=0 |
| Sampling | Ts=231.5 μs, one-sample computation delay |
| Sensor noise (std) | currents 5 A, DC voltage 1 V, grid voltage 1 V, encoder speed 2 mrad/s |
| Measurement filters | speed 5 ms, Pdc and vgd in (16) 2 ms, anemometer 1 s |

# 5. Numerical Simulations

This section presents the numerical results obtained with the proposed control. Two configurations are compared in order to assess the contribution of the adaptive network: the nominal flatness-based and passivity-based controller (Δ=0, with the integral action of the speed loop), and the same controller with the RBF compensation. The gains of Table 2 are the same in both configurations, so that any improvement can be attributed to the network.

The model is integrated with a fourth-order Runge–Kutta scheme at the step Ts over 40 s, starting from the maximum-power equilibrium. To obtain realistic results, the controller only uses measured signals: white noise is added to the current, voltage and speed measurements, the encoder speed is filtered, and the grid voltage contains background harmonics of order 5 (2 %, negative sequence) and 7 (1.5 %, positive sequence), i.e., a voltage distortion of 2.5 % (Table 2).

Two wind profiles are applied (Figure 4). The step profile (9 m/s, 11 m/s at 10 s and 8 m/s at 25 s), similar to the one of [18], assesses the transient response. The turbulent profile is

|  | vt=Vmean+k=13Aksin2πfkt+vturbt, | (28) |
| --- | --- | --- |

with Vmean=8.5 m/s, A=1.5, 0.2, 0.3 m/s and f=0.03, 0.16, 0.17 Hz [27]. The turbulence vturb is a first-order coloured noise with a standard deviation of 0.5 m/s and a correlation time of 1.5 s. Over 40 s, the turbulent wind remains between 6.0 and 10.9 m/s, below the rated wind speed. The controller uses the anemometer measurement vm, modeled by a first-order lag of 1 s.

Figure 4. Applied wind-speed profiles: (a) step profile; (b) turbulent profile.

Three cases are considered: (i) step wind with nominal parameters; (ii) turbulent wind with nominal parameters; (iii) robustness: turbulent wind, with a true plant that differs from the model of the controller (Cp×1.1, J×1.2, Rs×1.5, Ls×1.2, ψf×0.95, Rf×1.5, Lf×1.25), and a 50 % grid voltage dip between 25 and 25.15 s.

The speed tracking performance is evaluated with the speed error eΩt=Ωt−Ω*t, by the root-mean-square error, the mean absolute error, the maximum error, and the integral absolute and squared errors:

|  | RMSE=1Nk=1NeΩ2k, MAE=1Nk=1NeΩk, emax=maxkeΩk,IAE=∫eΩ dt, ISE=∫eΩ2 dt, | (29) |
| --- | --- | --- |

computed from t=1 s to t=40 s.

## 5.1. Step Wind

Figure 5 shows the references and the measured values of the controlled variables for the step wind with the RBF compensation. The rotor speed follows the MPPT reference from 1.82 to 2.23 and then 1.62 rad/s. The currents isq and igd follow their references during the transients, and isd and igq remain around zero, with the measurement noise and the 300 Hz ripple due to the grid harmonics. The DC-link voltage stays within 7 V (0.6 %) of 1200 V, since the generator power is passed to the grid through Pdc in (16).

Figure 5. Step wind, control with the RBF network: references (dashed) and measured values (solid) of the rotor speed, DC-link voltage, and stator and grid currents, with enlarged views of the step at 25 s.

## 5.2. Turbulent Wind and Robustness

Figure 6 shows the robustness case with the RBF compensation. The rotor speed follows its reference, and Cp stays close to its maximum, except during the fast wind decrease around 22 s, where the inertia prevents the rotor from slowing down quickly. The captured power follows the maximum available power, and the difference between the captured and the injected powers corresponds to the kinetic energy stored in or released by the rotor. The MPPT efficiency, i.e., the ratio between the captured energy and the maximum available energy, is 97.7 %.

Figure 6. Robustness case with the RBF network: rotor speed and reference, power coefficient (dotted: Cp,max of the true turbine), and maximum available, captured and injected powers.

## 5.3. Effect of the Adaptive Neural Compensation

Figure 7 compares the speed error without and with the network. For the step wind, the error after each step vanishes in about 1.9 s with the network instead of 3.9 s without it. In the turbulent cases, the error remains smaller, and the cumulative IAE grows more slowly over the whole simulation. Figure 8 shows that the network output follows the actual uncertainty; their mean values are 82.5 and 83.4 kN⋅m in the robustness case, i.e., about 14 % of the aerodynamic torque.

Figure 7. Speed tracking error without and with the RBF network: (a) step wind, with an enlarged view of the step at 25 s; (b) robustness case; (c) cumulative IAE for the three cases.

Figure 8. Robustness case: output Δ of the RBF network and actual uncertainty Δ (1-s average).

The speed tracking results are summarized in Table 3. With the network, the IAE decreases by 44.8 % for the step wind, 26.5 % for the turbulent wind and 27.9 % in the robustness case, and the ISE decreases by 46 to 52 %, while the nominal gains remain unchanged. Table 4 shows that the other variables are practically unchanged: the current errors, the DC-link deviation and the grid-current distortion are the same, and the captured energy and the MPPT efficiency are equal. The grid-current total harmonic distortion (THD), between 1.5 and 3.9 %, is below the 5 % limit of [31]. The price of the compensation is a slightly more active torque, with a 9 to 12 % larger standard deviation of its rate.

Table 3. Speed tracking performance of the nominal controller and of the controller with the adaptive RBF compensation (best values in bold).

| Case | Metric | Without ANN | With ANN | Improvement (%) |
| --- | --- | --- | --- | --- |
| Step wind | RMSE (mrad/s) | 4.99 | 3.67 | 26.5 |
|  | MAE (mrad/s) | 1.81 | 1.00 | 44.8 |
|  | emax (mrad/s) | 33.2 | 30.1 | 9.5 |
|  | IAE (mrad) | 70.6 | 39.0 | 44.8 |
|  | ISE (10−4 rad2/s) | 9.71 | 5.24 | 46.0 |
| Turbulent wind | RMSE (mrad/s) | 4.61 | 3.25 | 29.6 |
|  | MAE (mrad/s) | 3.63 | 2.66 | 26.5 |
|  | emax (mrad/s) | 12.7 | 7.42 | 41.4 |
|  | IAE (mrad) | 141.4 | 103.9 | 26.5 |
|  | ISE (10−4 rad2/s) | 8.28 | 4.11 | 50.4 |
| Robustness | RMSE (mrad/s) | 5.55 | 3.87 | 30.4 |
|  | MAE (mrad/s) | 4.47 | 3.22 | 27.9 |
|  | emax (mrad/s) | 14.2 | 8.93 | 37.0 |
|  | IAE (mrad) | 174.3 | 125.7 | 27.9 |
|  | ISE (10−4 rad2/s) | 12.0 | 5.83 | 51.5 |

Table 4. Performance of the whole system without and with the adaptive RBF compensation (40 s, from t=1 s; best values in bold, both in bold when the difference is negligible).

|  | Step wind |  | Turbulent wind |  | Robustness |  |
| --- | --- | --- | --- | --- | --- | --- |
| Metric | Without | With | Without | With | Without | With |
| Max Vdc−Vdc* (V)1 | 6.96 | 6.94 | 7.03 | 6.90 | 9.32 | 9.10 |
| RMS error of isq (A) | 5.83 | 5.80 | 5.85 | 5.81 | 5.81 | 5.79 |
| RMS error of igd (A) | 41.5 | 41.4 | 42.3 | 42.3 | 35.1 | 35.0 |
| Grid-current THD (%) | 1.45 | 1.45 | 3.86 | 3.92 | 2.55 | 2.58 |
| Energy (kWh) | 13.86 | 13.86 | 10.05 | 10.04 | 10.98 | 10.97 |
| MPPT efficiency (%) | 98.0 | 98.0 | 97.7 | 97.7 | 97.7 | 97.7 |
| Torque rate std (MN⋅m/s)2 | 0.239 | 0.267 | 0.212 | 0.231 | 0.210 | 0.233 |

1 outside the grid voltage dip; 2 of the torque averaged over 50 ms.

## 5.4. Grid Voltage Dip

Figure 9 shows the 50 % voltage dip of the robustness case. The grid current doubles, from 0.8 to 1.6 kA, to keep the injected power, which remains below the current limit of the converter. The DC-link voltage deviates by 16 V (1.3 %) at the beginning of the dip and returns within 5 V of 1200 V about 50 ms after the end of the dip.

Figure 9. Robustness case: grid voltage and current of phase a and DC-link voltage during the 50 % voltage dip (shaded).

# 6. Conclusions

This paper presented a flatness-based and passivity-based control with adaptive RBF neural compensation for a 2 MW direct-drive PMSG wind energy conversion system. The system was modeled from the wind to the grid in the receptor convention, and an exact power balance verified the signs of the model. The rotor speed and the energy of the DC link and of the filter were used as flat outputs, the currents of both converters were controlled by PBC with a proof of convergence, and an RBF network adapted by a Lyapunov-based law compensated the aerodynamic-torque and parameter uncertainty with uniformly ultimately bounded errors. Simulation results with sensor noise, grid harmonics, parameter mismatch and a voltage dip showed that all the controlled variables track their references, that the DC-link voltage remains within 0.8 % of its reference outside the dip, and that the network reduces the integral absolute speed error by 26.5 to 44.8 % with the same captured energy and the same nominal gains.

The proposed control has been validated by numerical simulations with the average model of the converters, so the switching ripple is not represented, and with an ideal synchronization to the grid. The turbulent wind was represented by one realization, and no experimental or hardware-in-the-loop (HIL) validation has yet been performed. Moreover, the stability analysis assumes that the current loops are fast with respect to the speed loop. These aspects will be addressed in future studies through a switching model with an LCL filter, the inclusion of the phase-locked loop dynamics, HIL implementation, and comparative evaluations with other control strategies.

Author Contributions: Conceptualization, M.M. and K.K.; Methodology, S.R.; Validation, S.R. and K.K.; Investigation, S.R.; Writing—original draft, S.R., M.M. and K.K.; Supervision, M.M. and K.K.; Project administration, M.M. and K.K. All authors have read and agreed to the published version of the manuscript.

Funding: This research received no external funding.

Data Availability Statement: The original contributions presented in this study are included in the article. Further inquiries can be directed to the corresponding author.

Conflicts of Interest: The authors declare no conflicts of interest.

# References

[1] Barthelmie, R.J.; Pryor, S.C. Climate Change Mitigation Potential of Wind Energy. Climate 2021, 9, 136. https://doi.org/10.3390/cli9090136.

[2] International Energy Agency (IEA). World Energy Outlook 2024; IEA: Paris, France, 2024.

[3] Global Wind Energy Council (GWEC). Global Wind Report 2024; GWEC: Brussels, Belgium, 2024.

[4] Polinder, H.; Ferreira, J.A.; Jensen, B.B.; Abrahamsen, A.B.; Atallah, K.; McMahon, R.A. Trends in Wind Turbine Generator Systems. IEEE J. Emerg. Sel. Top. Power Electron. 2013, 1, 174–185.

[5] Yaramasu, V.; Wu, B.; Sen, P.C.; Kouro, S.; Narimani, M. High-Power Wind Energy Conversion Systems: State-of-the-Art and Emerging Technologies. Proc. IEEE 2015, 103, 740–788.

[6] Wu, B.; Lang, Y.; Zargari, N.; Kouro, S. Power Conversion and Control of Wind Energy Systems; Wiley-IEEE Press: Hoboken, NJ, USA, 2011.

[7] Rolán, A.; Luna, A.; Vázquez, G.; Aguilar, D.; Azevedo, G. Modeling of a Variable Speed Wind Turbine with a Permanent Magnet Synchronous Generator. In Proceedings of the IEEE International Symposium on Industrial Electronics (ISIE), Seoul, Republic of Korea, 2009; pp. 734–739. https://doi.org/10.1109/ISIE.2009.5218120.

[8] Hasan, S.M.M.; Shatil, A.H.M. Design and Comparison of Grid Connected Permanent Magnet Synchronous Generator Non-Salient Pole and Salient Pole Rotor Wind Turbine. AIUB J. Sci. Eng. 2021, 20, 40–46.

[9] Chinchilla, M.; Arnaltes, S.; Burgos, J.C. Control of Permanent-Magnet Generators Applied to Variable-Speed Wind-Energy Systems Connected to the Grid. IEEE Trans. Energy Convers. 2006, 21, 130–135.

[10] Yazdani, A.; Iravani, R. Voltage-Sourced Converters in Power Systems: Modeling, Control, and Applications; Wiley-IEEE Press: Hoboken, NJ, USA, 2010.

[11] Blaabjerg, F.; Teodorescu, R.; Liserre, M.; Timbus, A.V. Overview of Control and Grid Synchronization for Distributed Power Generation Systems. IEEE Trans. Ind. Electron. 2006, 53, 1398–1409.

[12] Mechter, A.; Kemih, K.; Ghanes, M. Sliding Mode Control of a Wind Turbine with Exponential Reaching Law. Acta Polytech. Hung. 2015, 12, 167–183.

[13] Mechter, A.; Kemih, K.; Ghanes, M. Backstepping Control of a Wind Turbine for Low Wind Speeds. Nonlinear Dyn. 2016, 84, 2435–2445. https://doi.org/10.1007/s11071-016-2655-y.

[14] Messadi, M.; Mellit, A.; Kemih, K.; Ghanes, M. Predictive Control of a Chaotic Permanent Magnet Synchronous Generator in a Wind Turbine System. Chin. Phys. B 2015, 24, 010502.

[15] Yang, L.; Yang, F.; Sheng, W.; Zhou, K.; Huang, T. Fuzzy Chaos Control of Fractional Order D-PMSG for Wind Turbine with Uncertain Parameters by State Feedback Design. Energies 2021, 14, 7369.

[16] Benabdeeseelam, A.; Messadi, M.; Kemih, K.; Hamiche, H. Chattering-Free Terminal Sliding Mode Control Based on Adaptive Exponential Reaching Barrier Function for a Chaotic Permanent Magnet Synchronous Generator in Offshore Wind Turbine System. Chin. Phys. B 2025, 34, 090501.

[17] Fliess, M.; Lévine, J.; Martin, P.; Rouchon, P. Flatness and Defect of Non-Linear Systems: Introductory Theory and Examples. Int. J. Control 1995, 61, 1327–1361.

[18] Aimene, M.; Payman, A.; Dakyo, B. Comparative Study between Flatness-Based and Field-Oriented Control Methods of a Grid-Connected Wind Energy Conversion System. Processes 2022, 10, 378. https://doi.org/10.3390/pr10020378.

[19] Thounthong, P.; Pierfederici, S.; Davat, B. Analysis of Differential Flatness-Based Control for a Fuel Cell Hybrid Power Source. IEEE Trans. Energy Convers. 2010, 25, 909–920.

[20] Ortega, R.; Loría, A.; Nicklasson, P.J.; Sira-Ramírez, H. Passivity-Based Control of Euler-Lagrange Systems; Springer: London, UK, 1998.

[21] Ortega, R.; van der Schaft, A.; Maschke, B.; Escobar, G. Interconnection and Damping Assignment Passivity-Based Control of Port-Controlled Hamiltonian Systems. Automatica 2002, 38, 585–596.

[22] Park, J.; Sandberg, I.W. Universal Approximation Using Radial-Basis-Function Networks. Neural Comput. 1991, 3, 246–257.

[23] Lewis, F.L.; Jagannathan, S.; Yeşildirek, A. Neural Network Control of Robot Manipulators and Nonlinear Systems; Taylor & Francis: London, UK, 1999.

[24] Li, Y.; Sun, W.; Yu, D. RBFNN-Based Global Fast Terminal Sliding Mode Control for Fully Controlled Doubly Fed Induction Generator. J. Frankl. Inst. 2024, 361, 107196. https://doi.org/10.1016/j.jfranklin.2024.107196.

[25] Dardabi, C.; Djebli, A.; Chojaa, H. Enhancing the Control of Doubly Fed Induction Generators Using Artificial Neural Networks in the Presence of Real Wind Profiles. PLoS ONE 2024, 19, e0300527. https://doi.org/10.1371/journal.pone.0300527.

[26] Bounar, N.; Boulkroune, A.; Labdai, S.; Chrifi-Alaoui, L.; Khebbache, H. Disturbance Observer-Based Finite-Time Adaptive Neural Control Scheme of DFIG-Wind Turbine. Wind Eng. 2025, 49, 271–289. https://doi.org/10.1177/0309524X241263517.

[27] Regani, S.; Messadi, M.; Kemih, K. A Novel Chaos Control Approach with Adaptive ANN Compensation for a DFIG-Based Wind Turbine. Mathematics 2026, 14, 3739. https://doi.org/10.3390/math14203739.

[28] Heier, S. Grid Integration of Wind Energy: Onshore and Offshore Conversion Systems, 3rd ed.; Wiley: Chichester, UK, 2014.

[29] Khalil, H.K. Nonlinear Systems, 3rd ed.; Prentice Hall: Upper Saddle River, NJ, USA, 2002.

[30] Ioannou, P.A.; Sun, J. Robust Adaptive Control; Prentice Hall: Upper Saddle River, NJ, USA, 1996.

[31] IEEE Std 519-2014; IEEE Recommended Practice and Requirements for Harmonic Control in Electric Power Systems. IEEE: New York, NY, USA, 2014.